## Home
Boiler Energy Efficiency Self-Assessment Tool
Introduction: The Punjab Energy Efficiency and Conservation Authority (PEECA) of the Governnment of Punjab, Pakistan is working rigurously to improve energy efficiency and promote a culture of Energy Conservation in the province. To aide the efforts, PEECA has developed excel based self-assessment tools to calculate energy efficiency and enerrgy saving potentials in different industrial and commercial utilities.
About this tool: This tool calculates Required and Actual Energy for steam production, Specific Fuel Consumption, Steam Cost and Overall Efficiency of Boilers.
Version Information: Version No. V01_170304 Previous Version: N/A
How to Use? - Enter data in the "Data Input" sheet. Please refer to "Example Data" sheet for guidance to fill the data. - Blue tab sheets show results of calculations. - Purple tab sheets show reference data used for calculations - All Red labelled fields with white colored cells are data entry fields - All blue labelled fields with Grey colored cells are Calculation and Output Fields. - Please do not try to temper with any calculation cells as this will alter the results. Please contact PEECA or the developers for any alteration or change requests.
References: - Spirax Sarco Limited; http://www.spiraxsarco.com/pages/home.aspx - Improving Steam Boiler Operating Efficiency , by Enercon.gov.pk - Energy Technology Handbook, McGraw Hill, 9-46 - Saturated Steam Table by Pressure; http://www.tlv.com/global/TI/calculator/steam-table-pressure.html - https://www.engineersedge.com/thermodynamics/steam_tables.htm - Properties of Saturated Steam; http://www.engineeringtoolbox.com/saturated-steam-properties-d_457.html - Water Thermal Properties; http://www.engineeringtoolbox.com/water-thermal-properties-d_162.html - www.enggcyclopedia.com/2011/09/sample-problem-insulation-thickness-calculation-pipe/ - www.engineeringtoolbox.com/fiberglas-insulation-k-values-d_1172.html - www.engineeringtoolbox.com/mineral-wool-insulation-k-values-d_815.html - "INSULATION AND REFRACTORIES" by Bureau of Energy Efficiency India page 122-128, pdhonline.org/cources/m157/m157 content.pdf - http://www.infrared-thermography.com/material.htm - Estimating of cost steam lost through orifices(By Henry Manczyk, CPE, CEM); www.swagelokenergy.com/download/ECSLTOST.pdf - Bureau of energy efficiency India - Enorcon Pakistan - APO Japan - Excel add-in for Steam and Water Tables "Water97_v13.xla" by Bernhard Spang
Disclaimer: The information, calculations and conclusions in this tool are based on the sources as mentioned above. The tool has been field tested, however, qualified engineers must be consulted before makinng any decision based on these calculations. PEECA, Government of Punjab or the Developers accept no liability whatsoever to any person, company or entity for any injury, loss or damage that may arise in connection with any misuse or reliance on the information. The tool is provided as a freeware. Users may make copies and distribute the tool without making any changes.
Contact: Users may contact following for any clarification, suggestion and/or improvement in this tool;
Managing Director Punjab Energy Efficiency and Conservation Agency (PEECA) Energy Department, Government of the Punjab md.peeca@energy.punjab.gov.pk 48-A, Block C-II, Ghalib Road, Gulberg-III, Lahore Pakistan | Developer M. Salman Butt ESPIRE Consult +92 305 555 2343 salman@espire.com.pk 198 A-1, M. A. Jauhar Town, Lahore, Pakistan

## Data Input
Boiler Data Sheet
# | Boiler Code [Identity] | Boiler Heating Surface Area [m²] | Rated Boiler Capacity [kWhth] | Average Steam Production from Steam Flow Meter [Ton/h] | Steam Pressure [bar] | Steam Temperature [⁰C] | Specific Enthalpy of Steam [kJ/kg] | Specific Enthalpy of Steam [mmBtu/Ton] | Calculated Steam Production [Ton/h] | Calculated Steam Production [Ton/y] | Annual Operation [hrs/y] | Feed Water Temperature [⁰C] | Enthalpy of Feed Water [kJ/kg] | Enthalpy of Feed Water [mmBtu/Ton] | Net Energy Required [mmBtu/y] | Boiler Fuel | Fuel Price [PKR/ mmbtu] | Annual Fuel Consumption [mmbtu/y] | Specific Fuel Consumption [mmbtu/Ton] | Hourly Fuel Consumption [mmbtu/h] | Total Energy Cost [MPKR/y] | Steam Fuel Cost [PKR/Ton] | Net Boiler Efficiency [%]
[7 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
|  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [5 empty] | 0 | 0
0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | #DIV/0! |  |  |  | 0 |  | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!

## Dropdown (hidden)
Fuel | GCV Unit
Natural Gas | [btu/ftᶟ]
HFO | [kJ/kg]
Coal
Diesel
LPG
Bio Mass
Select

## Boiler Efficiency Dashboard
Boiler Efficiency Dashboard
Steam Production |  |  | Specific Energy Consumption
[5 empty] | Inlet velocity | #DIV/0! | m/s
No. of Boilers |  | Total Steam Production | Specific Fuel Consumption | Hourly Fuel Consumption | Outlet Velocity | #DIV/0! | m/s
0 |  | 0 | #DIV/0! | #DIV/0! | Inlet velocity head | #DIV/0! | m of head
Ton/y |  | Ton/y | mmBtu/Ton | mmBtu/h | outlet velocity head | #DIV/0! | m of head
Net Energy Requirement |  | Annual Energy Input | Total Energy Cost | Steam Cost (Fuel only)
0 |  | 0 | 0 | #DIV/0!
mmBtu/y |  | mmBtu/y | MPKR/y | PKR/Ton
Efficiency Calculations
|  | Max. Net Efficiency | Min. Net Efficiency
|  | 0% | 0%
|  | % | %
Overall Efficiency of Steam Boilers
#DIV/0!
%
EFFICIENCY | OPTIMIZATION GUIDELINES
75% | System is runnning well. Continuously monitor energy performance
70% | Automate Boiler Controls, Improve Fuel Properties
65% | Adjust Air:Fuel ratio, Check Insulations, Inspect Steam Traps and PRVs
60% | Pre-Heat Air and/or Feed Water, Conduct Boiler Maintenance
55% | Consult Expert; Boiler is Over Designed or Needs Replacement

## Steam and Water Table
Steam & Water Tables
Water Enthalpy Table |  |  |  | Saturated Steam Enthalpy Table
Temperature |  | Pressure | Specific enthalpy of liquid water * | Pressure |  | Specific enthalpy of Saturated Steam as function of Pressure *
°C | °K | Bar | kj/kg | Bar | psi | kj/kg
0 | 273.15 | 1.0132 | 0.061012 | 1 | 14.5038 | 2674.9496
1 | 274.15 | 1.0132 | 4.2787 | 2 | 29.0075 | 2706.2413
2 | 275.15 | 1.0132 | 8.4931 | 3 | 43.5113 | 2724.8917
3 | 276.15 | 1.0132 | 12.7046 | 4 | 58.0151 | 2738.0566
4 | 277.15 | 1.0132 | 16.9132 | 5 | 72.5189 | 2748.1076
5 | 278.15 | 1.0132 | 21.1194 | 6 | 87.0226 | 2756.1389
6 | 279.15 | 1.0132 | 25.3232 | 7 | 101.5264 | 2762.7491
7 | 280.15 | 1.0132 | 29.5249 | 8 | 116.0302 | 2768.3025
8 | 281.15 | 1.0132 | 33.7246 | 9 | 130.534 | 2773.0376
9 | 282.15 | 1.0132 | 37.9225 | 10 | 145.0377 | 2777.1195
10 | 283.15 | 1.0132 | 42.1187 | 11 | 159.5415 | 2780.6672
11 | 284.15 | 1.0132 | 46.3134 | 12 | 174.0453 | 2783.7691
12 | 285.15 | 1.0132 | 50.5067 | 13 | 188.5491 | 2786.4934
13 | 286.15 | 1.0132 | 54.6987 | 14 | 203.0528 | 2788.893
14 | 287.15 | 1.0132 | 58.8894 | 15 | 217.5566 | 2791.0105
15 | 288.15 | 1.0132 | 63.079 | 16 | 232.0604 | 2792.8804
16 | 289.15 | 1.0132 | 67.2676 | 17 | 246.5642 | 2794.5308
17 | 290.15 | 1.0132 | 71.4552 | 18 | 261.0679 | 2795.9855
18 | 291.15 | 1.0132 | 75.642 | 19 | 275.5717 | 2797.2643
19 | 292.15 | 1.0132 | 79.8279 | 20 | 290.0755 | 2798.3841
20 | 293.15 | 1.0132 | 84.0131 | 21 | 304.5792 | 2799.3594
21 | 294.15 | 1.0132 | 88.1975 | 22 | 319.083 | 2800.2027
22 | 295.15 | 1.0132 | 92.3813 | 23 | 333.5868 | 2800.9248
23 | 296.15 | 1.0132 | 96.5645 | 24 | 348.0906 | 2801.5354
24 | 297.15 | 1.0132 | 100.7472 | 25 | 362.5943 | 2802.0427
25 | 298.15 | 1.0132 | 104.9293 | 26 | 377.0981 | 2802.4543
26 | 299.15 | 1.0132 | 109.111 | 27 | 391.6019 | 2802.7766
27 | 300.15 | 1.0132 | 113.2922 | 28 | 406.1057 | 2803.0157
28 | 301.15 | 1.0132 | 117.4731 | 29 | 420.6094 | 2803.1768
29 | 302.15 | 1.0132 | 121.6535 | 30 | 435.1132 | 2803.2647
30 | 303.15 | 1.0132 | 125.8337 | 31 | 449.617 | 2803.2837
31 | 304.15 | 1.0132 | 130.0136 | 32 | 464.1208 | 2803.2377
32 | 305.15 | 1.0132 | 134.1932 | 33 | 478.6245 | 2803.1302
33 | 306.15 | 1.0132 | 138.3726 | 34 | 493.1283 | 2802.9645
34 | 307.15 | 1.0132 | 142.5518 | 35 | 507.6321 | 2802.7435
35 | 308.15 | 1.0132 | 146.7308 | 36 | 522.1359 | 2802.47
36 | 309.15 | 1.0132 | 150.9097 | 37 | 536.6396 | 2802.1464
37 | 310.15 | 1.0132 | 155.0885 | 38 | 551.1434 | 2801.7751
38 | 311.15 | 1.0132 | 159.2671 | 39 | 565.6472 | 2801.358
39 | 312.15 | 1.0132 | 163.4457 | 40 | 580.151 | 2800.8973
40 | 313.15 | 1.0132 | 167.6243 | 41 | 594.6547 | 2800.3947
41 | 314.15 | 1.0132 | 171.8029 | 42 | 609.1585 | 2799.8519
42 | 315.15 | 1.0132 | 175.9814 | 43 | 623.6623 | 2799.2703
43 | 316.15 | 1.0132 | 180.16 | 44 | 638.166 | 2798.6516
44 | 317.15 | 1.0132 | 184.3386 | 45 | 652.6698 | 2797.997
45 | 318.15 | 1.0132 | 188.5174 | 46 | 667.1736 | 2797.3078
46 | 319.15 | 1.0132 | 192.6962 | 47 | 681.6774 | 2796.5851
47 | 320.15 | 1.0132 | 196.8751 | 48 | 696.1811 | 2795.8301
48 | 321.15 | 1.0132 | 201.0542 | 49 | 710.6849 | 2795.0438
49 | 322.15 | 1.0132 | 205.2335 | 50 | 725.1887 | 2794.2271
50 | 323.15 | 1.0132 | 209.4129 | 51 | 739.6925 | 2793.3809
51 | 324.15 | 1.0132 | 213.5926 | 52 | 754.1962 | 2792.506
52 | 325.15 | 1.0132 | 217.7725 | 53 | 768.7 | 2791.6034
53 | 326.15 | 1.0132 | 221.9527 | 54 | 783.2038 | 2790.6736
54 | 327.15 | 1.0132 | 226.1331 | 55 | 797.7076 | 2789.7174
55 | 328.15 | 1.0132 | 230.3138 | 56 | 812.2113 | 2788.7354
56 | 329.15 | 1.0132 | 234.4949 | 57 | 826.7151 | 2787.7283
57 | 330.15 | 1.0132 | 238.6763 | 58 | 841.2189 | 2786.6967
58 | 331.15 | 1.0132 | 242.858 | 59 | 855.7227 | 2785.641
59 | 332.15 | 1.0132 | 247.0402 | 60 | 870.2264 | 2784.5617
60 | 333.15 | 1.0132 | 251.2227 | 61 | 884.7302 | 2783.4595
61 | 334.15 | 1.0132 | 255.4057 | 62 | 899.234 | 2782.3346
62 | 335.15 | 1.0132 | 259.5891 | 63 | 913.7377 | 2781.1876
63 | 336.15 | 1.0132 | 263.773 | 64 | 928.2415 | 2780.0189
64 | 337.15 | 1.0132 | 267.9574 | 65 | 942.7453 | 2778.8288
65 | 338.15 | 1.0132 | 272.1423 | 66 | 957.2491 | 2777.6176
66 | 339.15 | 1.0132 | 276.3278 | 67 | 971.7528 | 2776.3858
67 | 340.15 | 1.0132 | 280.5138 | 68 | 986.2566 | 2775.1336
68 | 341.15 | 1.0132 | 284.7003 | 69 | 1000.7604 | 2773.8613
69 | 342.15 | 1.0132 | 288.8875 | 70 | 1015.2642 | 2772.5692
70 | 343.15 | 1.0132 | 293.0753 | 71 | 1029.7679 | 2771.2576
71 | 344.15 | 1.0132 | 297.2637 | 72 | 1044.2717 | 2769.9268
72 | 345.15 | 1.0132 | 301.4528 | 73 | 1058.7755 | 2768.5769
73 | 346.15 | 1.0132 | 305.6425 | 74 | 1073.2793 | 2767.2081
74 | 347.15 | 1.0132 | 309.833 | 75 | 1087.783 | 2765.8208
75 | 348.15 | 1.0132 | 314.0242 | 76 | 1102.2868 | 2764.415
76 | 349.15 | 1.0132 | 318.2161 | 77 | 1116.7906 | 2762.991
77 | 350.15 | 1.0132 | 322.4088 | 78 | 1131.2944 | 2761.5489
78 | 351.15 | 1.0132 | 326.6022 | 79 | 1145.7981 | 2760.0889
79 | 352.15 | 1.0132 | 330.7965 | 80 | 1160.3019 | 2758.6111
80 | 353.15 | 1.0132 | 334.9916 | 81 | 1174.8057 | 2757.1157
81 | 354.15 | 1.0132 | 339.1875 | 82 | 1189.3095 | 2755.6028
82 | 355.15 | 1.0132 | 343.3844 | 83 | 1203.8132 | 2754.0725
83 | 356.15 | 1.0132 | 347.582 | 84 | 1218.317 | 2752.5249
84 | 357.15 | 1.0132 | 351.7807 | 85 | 1232.8208 | 2750.9602
85 | 358.15 | 1.0132 | 355.9802 | 86 | 1247.3245 | 2749.3784
86 | 359.15 | 1.0132 | 360.1807 | 87 | 1261.8283 | 2747.7796
87 | 360.15 | 1.0132 | 364.3821 | 88 | 1276.3321 | 2746.1639
88 | 361.15 | 1.0132 | 368.5846 | 89 | 1290.8359 | 2744.5313
89 | 362.15 | 1.0132 | 372.788 | 90 | 1305.3396 | 2742.8819
90 | 363.15 | 1.0132 | 376.9925 | 91 | 1319.8434 | 2741.2158
91 | 364.15 | 1.0132 | 381.1981 | 92 | 1334.3472 | 2739.5331
92 | 365.15 | 1.0132 | 385.4047 | 93 | 1348.851 | 2737.8336
93 | 366.15 | 1.0132 | 389.6125 | 94 | 1363.3547 | 2736.1175
94 | 367.15 | 1.0132 | 393.8213 | 95 | 1377.8585 | 2734.3848
95 | 368.15 | 1.0132 | 398.0313 | 96 | 1392.3623 | 2732.6356
96 | 369.15 | 1.0132 | 402.2424 | 97 | 1406.8661 | 2730.8697
97 | 370.15 | 1.0132 | 406.4548 | 98 | 1421.3698 | 2729.0872
98 | 371.15 | 1.0132 | 410.6683 | 99 | 1435.8736 | 2727.2882
99 | 372.15 | 1.0132 | 414.8831 | 100 | 1450.3774 | 2725.4726
100 | 373.15 | 1.0132 | 2675.5849 | 101 | 1464.8812 | 2723.6403
* Enthalpy is calculated using Excel add-in for Steam and Water Tables "Water97_v13.xla" by Bernhard Spang

## Example Data
Example Boiler Data Sheet
# | Boiler Code [Identity] | Boiler Heating Surface Area [m²] | Rated Boiler Capacity [kWhth] | Average Steam Production from Steam Flow Meter [Ton/h] | Steam Pressure [bar] | Steam Temperature [⁰C] | Specific Enthalpy of Steam [kJ/kg] | Specific Enthalpy of Steam [mmBtu/Ton] | Calculated Steam Production [Ton/h] | Calculated Steam Production [Ton/y] | Annual Operation [hrs/y] | Feed Water Temperature [⁰C] | Enthalpy of Feed Water [kJ/kg] | Enthalpy of Feed Water [mmBtu/Ton] | Net Energy Required [mmBtu/y] | Boiler Fuel | Fuel Price [PKR/ mmbtu] | Annual Fuel Consumption [mmbtu/y] | Specific Fuel Consumption [mmbtu/Ton] | Hourly Fuel Consumption [mmbtu/h] | Total Energy Cost [MPKR/y] | Steam Fuel Cost [PKR/Ton] | Net Boiler Efficiency [%]
1 | Boiler_001_ABC |  | 0 | 3 | 7 | 170 | 2762.7491 | 2.6166 | 3 | 7959 | 2653 | 35 | 146.7308 | 0.13897 | 19719.1788 | Natural Gas | 600 | 26483 | 3.3274 | 9.9823 | 15.8898 | 1996.4568 | 74.46%
2 | Boiler_002_ABC | 600 | 6000 | 7.5 | 7 | 175 | 2762.7491 | 2.6166 | 7.5 | 11250 | 1500 | 35 | 146.7308 | 0.13897 | 27872.944 | HFO | 900 | 35000 | 3.1111 | 23.3333 | 31.5 | 2800 | 79.64%
2 |  |  | 6000 | 10.5 |  |  |  |  | 10.5 | 19209 | 2076.5 |  |  |  | 47592.1227 |  | 750 | 61483 | 3.2193 | 16.6578 | 47.3898 | 2467.0623 | 77.05%